## Hydrotest_Report
HYDROSTATIC TEST REPORT
1. PROJECT & SYSTEM DETAILS
Project Name: | Cooling Water Expansion |  | Report No: | HTR-CW-001
System / Line No: | CW-10-CS-150 |  | Date of Test: | 2026-03-06
P&ID / Iso Drawing No: | ISO-CW-1001 Rev.2 |  | Material / Spec: | Carbon Steel A106 Gr.B
2. TEST PARAMETERS
Design Pressure: | 150 psig |  | Holding Time (Mins): | 60 Minutes
Required Test Pressure: | 225 psig (1.5x) |  | Gauge Calibration Date: | 2026-02-19
Test Medium: | Potable Water |  | Ambient Temp (°C/°F): | 22 °C
3. TEST LOG (PRESSURE & TEMPERATURE MONITORING)
Time | Elapsed (Mins) | Pressure Reading | Pipe Temp | Ambient Temp | Remarks / Observations
10:00 | 0 | 225 psig | 20 °C | 22 °C | Pressurization Complete. Hold starts.
10:30 | 30 | 225 psig | 20 °C | 23 °C | Pressure stable. No visible leaks.
11:00 | 60 | 224 psig | 21 °C | 24 °C | 1 psi drop (acceptable due to temp). Hold ends.
4. INSPECTION RESULTS & SIGNATURES
Visual Leaks Detected? |  | No |  | FINAL RESULT: | PASS
Contractor QC / Supervisor |  |  | Client Representative / Inspector
Name: |  |  | Name:
Sign: |  |  | Sign:
Date: |  |  | Date: